LOAD TEST CAT DIESEL GENERATOR SET

| Job data: |  |  |  |
| --- | --- | --- | --- |
| Customer: |  | WO |  |
| Site: | Zeppelin Esbjerg | Date | 05.09.2024 |
|  |  | Service engineer |  |
| Installation data: |  |  |  |
| Engine type: | C32 | Genset type: |  |
| Engine arr. no: | 485-8809 | Genset arr. no: |  |
| Engine serial no: | JPS00526 | Genset serial no: |  |
| Engine power: |  | Full load performance: | 970 |

LOAD TEST EPG ENGINE PROGRAM

FOR STABLE CONDITIONS - ENGINE RUNNING TIME: 15 MIN. BEFORE TEST START.

| 25% LOAD | 25 | MIN. RUNNING | REMARKS: |  |
| --- | --- | --- | --- | --- |
| 50% LOAD | 15 | MIN. RUNNING | REMARKS: |  |
| 75% LOAD | 15 | MIN. RUNNING | REMARKS: |  |
| 100% LOAD | 30 | MIN. RUNNING | REMARKS: |  |

PARTICIPANTS:

FROM: Zeppelin Power Systems: Erik P. Bundesen

FROM:

FROM:

FROM:

|  | LOAD TEST EPG |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- |
| HOUR |  | H/M | 10.00 | 10.40 | 10.55 | 11.10 | 11.25 |
| LOAD % |  | % | 25 | 50 | 75 | 100 | 100 |
| AMBIENT TEMPERATURE OUTSIDE |  | °C | 24,0 | 24,5 | 24,5 | 24,5 | 24,5 |
| RPM |  |  | 1500 | 1498 | 1500 | 1501 | 1500 |
| LUBE OIL PRESSURE |  | KPA | 427 | 406 | 391 | 379 | 374 |
| LUBE OIL TEMPERATURE BEFORE COOLER |  | °C | N/A | N/A | 92 | 96 | 100 |
| LUBE OIL TEMPERATURE AFTER COOLER |  | °C | N/A | N/A | 73 | 73 | 73 |
| COOLING WATER TEMPERATURE INLET ENGINE |  | °C | N/A | N/A | 63 | 63 | 69 |
| COOLING WATER TEMP OUTLET ENGINE |  | °C | 83 | 85 | 87 | 87 | 89 |
| AIR TEMP INLET A/C |  | °C | N/A | N/A | 140 | 186 | 189 |
| AIR TEMP OUTLET A/C |  | °C | 26,2 | N/A | 30,6 | 33,3 | 36,1 |
| BOOST PRESS. |  | KPA | 38 | 89 | 164 | 251 | 250 |
| FUEL PRESSURE |  | KPA | 700 | 692 | 694 | 678 | 672 |
| FUEL CONSUMPTION |  | L / HOUR | 65 | 113 | 185 | 235 | 235 |
| CRANKCASE PRESSURE |  | mm H2O | -1,0 | -1,0 | -0,9 | -0,7 | -0,7 |
| LOAD |  | KW | 241 | 482 | 726 | 967 | 960 |
| VOLTAGE |  | V | 398 | 398 | 398 | 398 | 398 |
| CURRENT |  | A. | 348 | 698 | 1055 | 1402 | 1397 |
| FREQUENCY |  | Hz | 50 | 50 | 50 | 50 | 50 |
| READING MADE BY: |  | INT. | EPB | EPB | EPB | EPB | EPB |

| COMMENTS: |  |
| --- | --- |